CEMLINE CORPORATION

# SSH SPECIFICATION

BOILER WATER AS ENERGY SOURCE

Semi-instantaneous heater shall be Cemline Series “SSH”; factory assembled and packaged.  Water heater shall be constructed in accordance with ASME Code for a working pressure of 150 psig.  The packaged water heater shall be constructed with a 316 stainless steel tank, with stainless threaded openings, 1/2" O.D. copper tubes, copper lined tube sheet, and steel or cast iron coil head.

Heater shall be mounted on a steel support skid.  Heater shall be insulated with 3" Fiberglass protected by an enameled metal jacket, 20 gauge minimum thickness.  Heater shall be factory assembled and piped including (air) (electronic) operated (2)  (3) way temperature regulating valve.  Coil shall have wrapper, shall be baffled and shall have an integral bronze valved circulator to circulate the water across the coil.

Heater shall be provided with a field programmable digital electronic limit control with LCD readout and digital thermometer.

Heater shall be furnished with a water pressure gauge and an A.S.M.E. pressure-temperature relief valve of sufficient size to relieve total BTU input of the coil.

Manufacturer shall assume responsibility for correct sizing of components to assure performance designated in design criteria.

Heater shall be CEMLINE Corporation Model insert__________.

Gallon capacity__________.

Coil to heat ______GPM from ______ oF to _____ oF with _____ GPM of _____ oF Hot Water.

OPTIONS

Coil shall be double walled 3/4" O.D. tubing with vented leak paths.

Furnish water heater with additional safety system designed to relieve excessively heated water from the vessel.  The safety system shall be field programmable for set point and differential and shall be of the electronic type.