# CEMLINE CORPORATION

USG SPECIFICATION- CARBON STEEL SHELL

HIGH TEMPERATURE HOT WATER AS ENERGY SOURCE

Unfired Steam Generator shall be as manufactured by Cemline Corporation, Cheswick, PA 15024.

Unfired Steam Generator shall be furnished as a complete package ready for installation.

Unfired Steam Generator shall be ASME Code constructed and stamped in accordance with Section VIII, Division I, for Unfired Steam Generators.  Unfired Steam Generators shall be registered with the National Board of Boiler and Pressure Vessel Inspectors, and signed copy of shop inspection report shall be furnished.  Unfired Steam Generator shall be built in accordance with Section VIII "Unfired Steam Generators" and shall bear the "UB" stamp.

Unfired Steam Generator and all components subject to steam side shall be carbon steel.

Unfired Steam Generator shall be insulated with not less than 3" of Fiberglass insulation, protected by not less than 20-ga. thick-enameled steel jacket.

Unfired Steam Generator shall be mounted on a suitable I-Beam support skid, which shall be permanently welded to the shell.

Unfired Steam Generator shall have submerged coil of 18 BWG copper tubes expanded into a steel tube sheet with fabricated steelheads.

Unfired Steam Generator shall be furnished with an (air) (electronic) operated (2) (3) - way control valve to modulate the in-coming HTHW to maintain the desired output of steam pressure +2 psi.  Control valve shall be suitable for 400 psi at 400oF.  Control valve pilot shall monitor output steam pressure and modulate the HTHW to maintain constant output pressure.

Unfired Steam Generator shall be furnished with an ASME Code Section I pressure relief valve

or valves with a capacity to relieve the total BTU of output of the generator.

Unfired Steam Generator shall be furnished with a vessel steam gauge, thermometer to monitor

the incoming HTHW temperature. Unfired Steam Generator shall be furnished with

float type level controller.  Water column shall also be furnished with gauge glass.

Unfired Steam Generator shall be furnished with tandem blow off valves.

All components for the Unfired Steam Generator shall be factory mounted, piped, and tested and

the unit shall be shipped from the factory as a complete unit ready for installation.  Unfired Steam

Generator shall be furnished with a steam separator.

Unfired steam generator shall be supplied with solid-state control module with LED backlit LCD display and LED pilot lights to indicate on off, high pressure, low pressure, low water, and water feed.  Solid-state control module shall allow the owner to set pressure limits on display screen.  Solid-state control module shall have flashing red alarm light and alarm horn with built in alarm silence relay.  Solid-state control module shall be supplied with dry contact closure outputs to indicate to building automation controls (BAC) the occurrence of power on, high pressure, low pressure, low water, and water feed.  The control module shall allow the BAC to turn the unfired steam generator on or off through a remote relay suitable for 24 VAC, 1 amp. The control module shall allow the BAC to remotely monitor the operating pressure.  Control module shall be supplied with an on-off switch and shall be mounted in a NEMA 1 panel.  All solenoids and limits shall be 24 VAC.

Furnish a factory installed brass feed water solenoid valve sized to feed the capacity of the boiler with a maximum pressure drop of 5 psi.  Solenoid valve shall be factory wired to the level controller.  Furnish a factory installed check valve between the solenoid valve and Unfired Steam Generator.

Unfired Steam Generator shall be Cemline Model ______________, designed with an output of ______ pound per hour at_____   psi pressure and feed water of _____        OF.

when supplied with _______ GPM of _________  oF boiler water.

OPTIONS

- VACUUM BREAKER

Package shall be supplied with vacuum breaker.

- ALARM BELL

Package shall be supplied with alarm bell and light to signal low water or high pressure.  Alarm silence relay shall be provided to silence the bell but not the light.

- REMOTE CONTROL

Package shall be provided with relay with 120-volt coil to remotely start or stop the Generator.

- CENTRIFUGAL BOILER BLOW OFF CONDENSATE COOLER

Package shall include a centrifugal boiler blow off condensate cooler.

- HIGH WATER CUT-OFF (PERSON CHOOSES BETWEEN AIR/ELETRIC)

High water shut off shall be factory furnished.  High water cut off shall be factory furnished.  High water cut off shall include an electronic probe mounted in the top of the unit connected to an (air) (electric)  operated power to open spring to close ball valve.  In the event of high water, ball valve will close.

- ADDITIONAL MAKE UP WATER FEEDING OPTIONS

- FEED WATER CONDENSATE PUMP WITH RECIEVER:

Furnish a factory installed feed water condensate system consisting of a receiver, inlet strainer, pump, water make up assembly, NEMA 1 panel with fused starter.  Furnish factory installed check valve between the feed water condensate system and the unfired steam generator.  Pump shall be factory wired to level controller.

- FEED WATER PUMP:

Furnish and install a feed water pump with flexible connector, shut off valve, and check valve.  Feed water pump shall be factory wired to level controller and furnished with fused starter in NEMA 1 enclosure.

AUTOMATIC BLOWDOWN (CHOOSE ONE)

- AUTOMATIC BLOWDOWN TIMER

Furnish a factory installed timed blowdown system consisting of a 24 hour, 7-day time clock and a 2 to 180 second interval timer and solenoid valve for blowing off the unfired steam generator.  Controls shall be factory wired and mounted in the NEMA 1 control panel with single point connection for the contractor to furnish 120 volts for operation of the automatic blowdown system.”

- AUTOMATIC BLOWDOWN TDS SAMPLING METHOD

Time sample feed water system.  Furnish a factory installed time sample feed water system consisting of a control which measures the total dissolved solids of the unfired steam generator on a timed basis.  If the total dissolved solids exceed the set point shall blow the boiler off until fresh water brings the total dissolved solids level to the desired setting.  Automatic blow off system shall be furnished with a NEMA 1 control system and all factory wired to a single point 120 volt connection.