CEMLINE CORPORATION

CST - CEMENT LINED TANK SPECIFICATION

CEMLINE STONESTEEL storage tank shall be furnished. The steel storage tank shall be constructed in accordance with Section IV of the ASME Code for 125 psig working pressure. The tank shall be registered with the National Board of Boiler and Pressure Vessel Inspectors and Certificate of Shop Inspection shall be furnished. The tank shall be lined with not less than 1/2" thick STONESTEEL cement lining, and all threaded openings shall be non-corrosive. Tanks above 36" diameter shall have wire mesh completely welded over the interior prior to application of lining. An 11" x 15" manhole shall be furnished as required by ASME Code on tanks above 400 gallon storage capacity. Tank shall be mounted (horizontally on saddles) (vertically with supports for pipe legs) (vertically with angle legs) (vertically with ring base).

Heater shall be CEMLINE Corporation Model _______________

Tank dimensions ___" diameter x  ____" length.

OPTIONAL COIL

Tank shall be furnished with a submerged u-bend coil with 3/4" O.D. copper tubes, copper lined tubesheet, and steel or cast iron coil head. The coil shall be designed to heat ______ GPH from ____ °F to ____  °F with (_____psig steam) (_______ GPM _____ °F boiler water).